## IFMR >10,000
INDIVIDUAL FILTER TURBIDITY MONITORING REPORT
(Systems Serving >10,000 People)
PWS NAME | [8 empty] | MONTH |  |  |  | YR
PWS ID # | [5 empty] | WTP NAME
| Total # of Filters at WTP |  |  |  |  | Total # of Filters in service during the month
Note: Individual Filters must be monitored continuously, results recorded every 15 minutes and maintained for 3 years.
Provide the filter # of each filter in service during the month.
List filter # of any filter(s) not continuously monitored using on-line turbidity meter. | [12 empty] | (Attach reason.)
Did you have a failure of any on-line turbidity meter? | [6 empty] | Yes |  | No |  | Number of days off-line?
Note: If individual filter turbidity monitor fails you must conduct grab samples every four hours and record results.
The individual filter turbidity monitor must be repaired and placed back on-line with in 5 working days.
Were any trigger levels exceeded? |  |  |  | Yes |  | No |  | If yes, complete the applicable sections below.
Filter # | Value in NTU of Turbidity Measurements > 1.0 in 2 Consecutive Measurements Taken 15 Minutes Apart -- During Normal Operation | [5 empty] | Conduct a Filter Profile Within 7 Days of the Exceedance(s) or Determine Obvious Reason for Abnormal Filter Performance
(Attach Filter Profile Report or Attach Report Outlining Obvious Reason for Exceedance)
| Date | Initial Reading Exceeding 1.0 |  | 2nd Reading Exceeding 1.0 |  |  | Date Profile Conducted |  |  |  |  | Date Obvious Reason for Exceedance Determined
Filter # | Value in NTU of Turbidity Measurements > 1.0 in 2 Consecutive Measurements Taken 15 Minutes Apart -- At Any Time In Each of Three Consecutive Months | [9 empty] | Conduct a Self-Assessment of the Filter Within 14 Days of the Exceedance
| Turbidity Exceeding 1.0 NTU | [9 empty] | (Attach Report of Filter Assessment)
| 1st Month |  | 2nd Month |  |  |  | 3rd Month
| Date | Value | Date |  | Value |  | Date |  | Value |  | Date Completed
The above figures are true and accurate to the best of my knowledge.
SIGNATURE | [5 empty] | DATE |  |  | POSITION
Page 1 of 2
INDIVIDUAL FILTER TURBIDITY MONITORING REPORT
PWS NAME | [8 empty] | MONTH |  |  |  | YR
PWS ID # | [8 empty] | WTP NAME
Filter # | Value in NTU of Turbidity Measurements > 0.5 in 2 Consecutive Measurements Taken 15 Minutes Apart -- At the End of the First 4 Hours of Continuous Filter Operation After the Filter Has Been Backwashed or Otherwise Taken Off Line | [5 empty] | Conduct a Filter Profile Within 7 Days of the Exceedance(s) or Determine Obvious Reason for Abnormal Filter Performance
(Attach Filter Profile Report or Attach Report Outlining Obvious Reason for Exceedance)
| Date | Initial Reading Exceeding 0.5 |  | 2nd Reading Exceeding 0.5 |  |  | Date Profile Conducted |  |  |  |  | Date Obvious Reason for Exceedance Determined
Filter # | Value in NTU of Turbidity Measurements > 2.0 in 2 Consecutive Measurements Taken 15 Minutes Apart -- At Any Time In Each of Two Consecutive Months | [5 empty] | Within 30 Days of the Exceedance the System Must Arrange Through the ADH to Have a CPE Conducted
(Within 90 Days of the Exceedance a CPE Must Be Completed and the CPE Report Submitted to the ADH)
| Turbidity Exceeding 2.0 NTU | [5 empty] | Date CPE Arrangements Completed |  |  |  |  | Date CPE Completed and Report Submitted to ADH
| 1st Month |  | 2nd Month
| Date | Value | Date |  | Value
The above figures are true and accurate to the best of my knowledge.
SIGNATURE | [5 empty] | DATE |  |  |  | POSITION
Make a copy for your records & return by the 10th of the following month to: | [8 empty] | ARKANSAS DEPT. OF HEALTH
ENGINEERING BRANCH
4815 WEST MARKHAM STREET, SLOT 37
LITTLE ROCK, AR 72205-3867
IFMR(large)-2027 | [12 empty] | Page 2 of 2